{"text_format":"3","workbook":"xlsx","n_sheets":7,"sheets":["记录","只读状态量","只读模拟量","读写模拟量","设备使能","输入端口配置","输出端口配置"],"read":"whole","date_system":"1900"}

{"sheet":"记录","index":0,"n_rows":2,"n_cols":4,"rows_kept":2}
[]
[null,"版本","记录","日期"]

{"sheet":"只读状态量","index":1,"n_rows":292,"n_cols":9,"rows_kept":292,"merged":[[0,1,0,5],[0,6,0,8]]}
[null,"02功能码读，出厂告警使能0表示使能，1表示禁止",{"$nulls":4},"06功能码写"]
[null,"地址","变量名称","类型","说明","出厂使能","告警使能设置寄存器","名称","值（十六进制）"]
[null,20000,"综合告警","Bit","0：正常；1：告警",0,30429,"告警使能1",{"$f":"DEC2HEX(F3+F4*2+F5*4+F6*8+F7*16+F8*32+F9*64+F10*128+F11*256+F12*512+F13*1024+F14*2048+F15*4096+F16*8192+F17*16384+F18*32768)","v":"0"}]
[null,20001,"回风高温","Bit","0：正常；1：告警",0,30430,"告警使能2",{"$f":"DEC2HEX(F19+F20*2+F21*4+F22*8+F23*16+F24*32+F25*64+F26*128+F27*256+F28*512+F29*1024+F30*2048+F31*4096+F32*8192+F33*16384+F34*32768)","v":"0"}]
[null,20002,"回风低温","Bit","0：正常；1：告警",0,30431,"告警使能3",{"$f":"DEC2HEX(F35+F36*2+F37*4+F38*8+F39*16+F40*32+F41*64+F42*128+F43*256+F44*512+F45*1024+F46*2048+F47*4096+F48*8192+F49*16384+F50*32768)","v":"0"}]
[null,20003,"回风高湿","Bit","0：正常；1：告警",0,30432,"告警使能4",{"$f":"DEC2HEX(F51+F52*2+F53*4+F54*8+F55*16+F56*32+F57*64+F58*128+F59*256+F60*512+F61*1024+F62*2048+F63*4096+F64*8192+F65*16384+F66*32768)","v":"0"}]
[null,20004,"回风低湿","Bit","0：正常；1：告警",0,30433,"告警使能5",{"$f":"DEC2HEX(F67+F68*2+F69*4+F70*8+F71*16+F72*32+F73*64+F74*128+F75*256+F76*512+F77*1024+F78*2048+F79*4096+F80*8192+F81*16384+F82*32768)","v":"0"}]
[null,20005,"送风高温","Bit","0：正常；1：告警",0,30434,"告警使能6",{"$f":"DEC2HEX(F83+F84*2+F85*4+F86*8+F87*16+F88*32+F89*64+F90*128+F91*256+F92*512+F93*1024+F94*2048+F95*4096+F96*8192+F97*16384+F98*32768)","v":"0"}]
[null,20006,"送风低温","Bit","0：正常；1：告警",0,30435,"告警使能7",{"$f":"DEC2HEX(F99+F100*2+F101*4+F102*8+F103*16+F104*32+F105*64+F106*128+F107*256+F108*512+F109*1024+F110*2048+F111*4096+F112*8192+F113*16384+F114*32768)","v":"0"}]
[null,20007,"开关机状态","Bit","0：关机；1：开机",0,30436,"告警使能8",{"$f":"DEC2HEX(F115+F116*2+F117*4+F118*8+F119*16+F120*32+F121*64+F122*128+F123*256+F124*512+F125*1024+F126*2048+F127*4096+F128*8192+F129*16384+F130*32768)","v":"0"}]
[null,20008,"烟雾报警","Bit","0：正常；1：告警",0,30437,"告警使能9",{"$f":"DEC2HEX(F131+F132*2+F133*4+F134*8+F135*16+F136*32+F137*64+F138*128+F139*256+F140*512+F141*1024+F142*2048+F143*4096+F144*8192+F145*16384+F146*32768)","v":"0"}]
[null,20009,"水浸报警","Bit","0：正常；1：告警",0,30438,"告警使能10",{"$f":"DEC2HEX(F147+F148*2+F149*4+F150*8+F151*16+F152*32+F153*64+F154*128+F155*256+F156*512+F157*1024+F158*2048+F159*4096+F160*8192+F161*16384+F162*32768)","v":"0"}]
[null,20010,"排水故障","Bit","0：正常；1：告警",0,30439,"告警使能11",{"$f":"DEC2HEX(F163+F164*2+F165*4+F166*8+F167*16+F168*32+F169*64+F170*128+F171*256+F172*512+F173*1024+F174*2048+F175*4096+F176*8192+F177*16384+F178*32768)","v":"0"}]
[null,20011,"冷凝排水泵","Bit","0：关；1：开",0,30440,"告警使能12",{"$f":"DEC2HEX(F179+F180*2+F181*4+F182*8+F183*16+F184*32+F185*64+F186*128+F187*256+F188*512+F189*1024+F190*2048+F191*4096+F192*8192+F193*16384+F194*32768)","v":"0"}]
[null,20012,"保留","Bit",null,0,30441,"告警使能13",{"$f":"DEC2HEX(F195+F196*2+F197*4+F198*8+F199*16+F200*32+F201*64+F202*128+F203*256+F204*512+F205*1024+F206*2048+F207*4096+F208*8192+F209*16384+F210*32768)","v":"0"}]
[null,20013,"保留","Bit",null,0,30442,"告警使能14",{"$f":"DEC2HEX(F211+F212*2+F213*4+F214*8+F215*16+F216*32+F217*64+F218*128+F219*256+F220*512+F221*1024+F222*2048+F223*4096+F224*8192+F225*16384+F226*32768)","v":"0"}]
[null,20014,"保留","Bit",null,0,30443,"告警使能15",{"$f":"DEC2HEX(F227+F228*2+F229*4+F230*8+F231*16+F232*32+F233*64+F234*128+F235*256+F236*512+F237*1024+F238*2048+F239*4096+F240*8192+F241*16384+F242*32768)","v":"0"}]
[null,20015,"保留","Bit",null,0,30444,"告警使能16",{"$f":"DEC2HEX(F243+F244*2+F245*4+F246*8+F247*16+F248*32+F249*64+F250*128+F251*256+F252*512+F253*1024+F254*2048+F255*4096+F256*8192+F257*16384+F258*32768)","v":"0"}]
[null,20016,"保留","Bit",null,0,30445,"告警使能17",{"$f":"DEC2HEX(F259+F260*2+F261*4+F262*8+F263*16+F264*32+F265*64+F266*128+F267*256+F268*512+F269*1024+F270*2048+F271*4096+F272*8192+F273*16384+F274*32768)","v":"0"}]
[null,20017,"A相过电压","Bit","0：正常；1：告警",0,30446,"告警使能18",{"$f":"DEC2HEX(F275+F276*2+F277*4+F278*8+F279*16+F280*32+F281*64+F282*128+F283*256+F284*512+F285*1024+F286*2048+F287*4096+F288*8192+F289*16384+F290*32768)","v":"0"}]
[null,20018,"B相过电压","Bit","0：正常；1：告警",0,30447,"告警使能19",{"$f":"DEC2HEX(F291+F292*2+F293*4+F294*8+F295*16+F296*32+F297*64+F298*128+F299*256+F300*512+F301*1024+F302*2048+F303*4096+F304*8192+F305*16384+F306*32768)","v":"0"}]
[null,20019,"C相过电压","Bit","0：正常；1：告警",0,30448,"告警使能20",{"$f":"DEC2HEX(F307+F308*2+F309*4+F310*8+F311*16+F312*32+F313*64+F314*128+F315*256+F316*512+F317*1024+F318*2048+F319*4096+F320*8192+F321*16384+F322*32768)","v":"0"}]
[null,20020,"A相欠电压","Bit","0：正常；1：告警",0,30449,"告警使能21",{"$f":"DEC2HEX(F323+F324*2+F325*4+F326*8+F327*16+F328*32+F329*64+F330*128+F331*256+F332*512+F333*1024+F334*2048+F335*4096+F336*8192+F337*16384+F338*32768)","v":"0"}]
[null,20021,"B相欠电压","Bit","0：正常；1：告警",0,30450,"告警使能22",{"$f":"DEC2HEX(F339+F340*2+F341*4+F342*8+F343*16+F344*32+F345*64+F346*128+F347*256+F348*512+F349*1024+F350*2048+F351*4096+F352*8192+F353*16384+F354*32768)","v":"0"}]
[null,20022,"C相欠电压","Bit","0：正常；1：告警",0,30451,"告警使能23",{"$f":"DEC2HEX(F355+F356*2+F357*4+F358*8+F359*16+F360*32+F361*64+F362*128+F363*256+F364*512+F365*1024+F366*2048+F367*4096+F368*8192+F369*16384+F379*32768)","v":"0"}]
[null,20023,"三相不平衡","Bit","0：正常；1：告警",0,30452,"告警使能24",{"$f":"DEC2HEX(F371+F372*2+F373*4+F374*8+F375*16+F376*32+F377*64+F378*128+F379*256+F380*512+F381*1024+F382*2048+F383*4096+F384*8192+F385*16384+F386*32768)","v":"0"}]
[null,20024,"源频率超下限","Bit","0：正常；1：告警",0,30453,"告警使能25",{"$f":"DEC2HEX(F387+F388*2+F389*4+F390*8+F391*16+F392*32+F393*64+F394*128+F395*256+F396*512+F397*1024+F398*2048+F399*4096+F400*8192+F401*16384+F402*32768)","v":"0"}]
[null,20025,"源频率超上限","Bit","0：正常；1：告警",0]
[null,20026,"A相缺相","Bit","0：正常；1：告警",0]
[null,20027,"B相缺相","Bit","0：正常；1：告警",0]
[null,20028,"C相缺相","Bit","0：正常；1：告警",0]
[null,20029,"电源错相","Bit","0：正常；1：告警",0]
[null,20030,"内风机1状态","Bit","0：关；1：开",0]
[null,20031,"内风机2状态","Bit","0：关；1：开",0]
[null,20032,"内风机3状态","Bit","0：关；1：开",0]
[null,20033,"内风机1故障","Bit","0：正常；1：告警",0]
[null,20034,"内风机2故障","Bit","0：正常；1：告警",0]
[null,20035,"内风机3故障","Bit","0：正常；1：告警",0]
[null,20036,"气流丢失","Bit","0：正常；1：告警",0]
[null,20037,"过滤网堵塞","Bit","0：正常；1：告警",0]
[null,20038,"滤网维护时间到","Bit","0：正常；1：告警",0]
[null,20039,"保留","Bit",null,0]
[null,20040,"保留","Bit",null,0]
[null,20041,"压缩机1状态","Bit","0：关；1：开",0]
[null,20042,"压缩机1加热带","Bit","0：关；1：开",0]
[null,20043,"压缩机1高压告警","Bit","0：正常；1：告警",0]
[null,20044,"压缩机1高压告警锁定","Bit","0：正常；1：告警",0]
[null,20045,"压缩机1低压告警","Bit","0：正常；1：告警",0]
[null,20046,"压缩机1低压告警锁定","Bit","0：正常；1：告警",0]
[null,20047,"压缩机1排气高温","Bit","0：正常；1：告警",0]
[null,20048,"压缩机1排气高温锁定","Bit","0：正常；1：告警",0]
[null,20049,"压缩机1频率异常","Bit","0：正常；1：告警",0]
[null,20050,"压缩机1频率异常锁定","Bit","0：正常；1：告警",0]
[null,20051,"压缩机1高压限频输出","Bit","0：关；1：开",0]
[null,20052,"EEV1启动压差异常","Bit","0：正常；1：告警",0]
[null,20053,"液管电磁阀1","Bit","0：关；1：开",0]
[null,20054,"外风机1状态","Bit","0：关；1：开",0]
[null,20055,"外风机1告警","Bit","0：正常；1：告警",0]
[null,20056,"保留","Bit",null,0]
[null,20057,"保留","Bit",null,0]
[null,20058,"保留","Bit",null,0]
[null,20059,"保留","Bit",null,0]
[null,20060,"压缩机2状态","Bit","0：关；1：开",0]
[null,20061,"压缩机2加热带","Bit","0：关；1：开",0]
[null,20062,"压缩机2高压告警","Bit","0：正常；1：告警",0]
[null,20063,"压缩机2高压告警锁定","Bit","0：正常；1：告警",0]
[null,20064,"压缩机2低压告警","Bit","0：正常；1：告警",0]
[null,20065,"压缩机2低压告警锁定","Bit","0：正常；1：告警",0]
[null,20066,"压缩机2排气高温","Bit","0：正常；1：告警",0]
[null,20067,"压缩机2排气高温锁定","Bit","0：正常；1：告警",0]
[null,20068,"压缩机2频率异常","Bit","0：正常；1：告警",0]
[null,20069,"压缩机2频率异常锁定","Bit","0：正常；1：告警",0]
[null,20070,"压缩机2高压限频输出","Bit","0：关；1：开",0]
[null,20071,"EEV2启动压差异常","Bit","0：正常；1：告警",0]
[null,20072,"液管电磁阀2","Bit","0：关；1：开",0]
[null,20073,"外风机2状态","Bit","0：关；1：开",0]
[null,20074,"外风机2告警","Bit","0：正常；1：告警",0]
[null,20075,"保留","Bit",null,0]
[null,20076,"保留","Bit",null,0]
[null,20077,"保留","Bit",null,0]
[null,20078,"保留","Bit",null,0]
[null,20079,"变频器1故障","Bit","0：正常；1：告警",0]
[null,20080,"变频器1通讯故","Bit","0：正常；1：告警",0]
[null,20081,"变频器1加速过流","Bit","0：正常；1：告警",0]
[null,20082,"变频器1减速过流","Bit","0：正常；1：告警",0]
[null,20083,"变频器1恒速过流","Bit","0：正常；1：告警",0]
[null,20084,"变频器1变频器严重故障","Bit","0：正常；1：告警",0]
[null,20085,"变频器1加速过压","Bit","0：正常；1：告警",0]
[null,20086,"变频器1减速过压","Bit","0：正常；1：告警",0]
[null,20087,"变频器1恒速过压","Bit","0：正常；1：告警",0]
[null,20088,"变频器1母线欠压","Bit","0：正常；1：告警",0]
[null,20089,"变频器1电机过载","Bit","0：正常；1：告警",0]
[null,20090,"变频器1过载","Bit","0：正常；1：告警",0]
[null,20091,"变频器1输入缺相","Bit","0：正常；1：告警",0]
[null,20092,"变频器1输出缺相","Bit","0：正常；1：告警",0]
[null,20093,"变频器1缓冲电阻故障","Bit","0：正常；1：告警",0]
[null,20094,"变频器1模块过热","Bit","0：正常；1：告警",0]
[null,20095,"变频器1变频器通讯故障","Bit","0：正常；1：告警",0]
[null,20096,"变频器1电流检测故障","Bit","0：正常；1：告警",0]
[null,20097,"变频器1EEPROM故障","Bit","0：正常；1：告警",0]
[null,20098,"变频器1对地短路故障1 ","Bit","0：正常；1：告警",0]
[null,20099,"变频器1硬件/对地短路2故障","Bit","0：正常；1：告警",0]
[null,20100,"变频器1速度偏差故障","Bit","0：正常；1：告警",0]
[null,20101,"变频器1失调故障","Bit","0：正常；1：告警",0]
[null,20102,"变频器1欠载故障","Bit","0：正常；1：告警",0]
[null,20103,"变频器1电子过载故障","Bit",null,0]
[null,20104,"变频器1自学习故障","Bit",null,0]
[null,20105,"变频器2故障","Bit","0：正常；1：告警",0]
[null,20106,"变频器2通讯故障2","Bit","0：正常；1：告警",0]
[null,20107,"变频器2加速过流","Bit","0：正常；1：告警",0]
[null,20108,"变频器2减速过流","Bit","0：正常；1：告警",0]
[null,20109,"变频器2恒速过流","Bit","0：正常；1：告警",0]
[null,20110,"变频器2严重故障","Bit","0：正常；1：告警",0]
[null,20111,"变频器2加速过压","Bit","0：正常；1：告警",0]
[null,20112,"变频器2减速过压","Bit","0：正常；1：告警",0]
[null,20113,"变频器2恒速过压","Bit","0：正常；1：告警",0]
[null,20114,"变频器2母线欠压","Bit","0：正常；1：告警",0]
[null,20115,"变频器2电机过载","Bit","0：正常；1：告警",0]
[null,20116,"变频器2过载","Bit","0：正常；1：告警",0]
[null,20117,"变频器2输入缺相","Bit","0：正常；1：告警",0]
[null,20118,"变频器2输出缺相","Bit","0：正常；1：告警",0]
[null,20119,"变频器2缓冲电阻故障","Bit","0：正常；1：告警",0]
[null,20120,"变频器2模块过热","Bit","0：正常；1：告警",0]
[null,20121,"变频器2通讯故障","Bit","0：正常；1：告警",0]
[null,20122,"变频器2电流检测故障","Bit","0：正常；1：告警",0]
[null,20123,"变频器2EEPROM故障","Bit","0：正常；1：告警",0]
[null,20124,"变频器2对地短路故障1","Bit","0：正常；1：告警",0]
[null,20125,"变频器2硬件/对地短路2故障","Bit","0：正常；1：告警",0]
[null,20126,"变频器2速度偏差故障","Bit","0：正常；1：告警",0]
[null,20127,"变频器2失调故障","Bit","0：正常；1：告警",0]
[null,20128,"变频器2欠载故障","Bit","0：正常；1：告警",0]
[null,20129,"变频器2电子过载故障","Bit",null,0]
[null,20130,"变频器2自学习故障","Bit",null,0]
[null,20131,"加湿器状态","Bit","0：关；1：开",0]
[null,20132,"加湿器故障","Bit","0：正常；1：告警",0]
[null,20133,"加湿电流检测故障","Bit","0：正常；1：告警",0]
[null,20134,"加湿桶排水故障","Bit","0：正常；1：告警",0]
[null,20135,"湿膜低水位","Bit","0：正常；1：告警",0]
[null,20136,"水位开关故障","Bit","0：正常；1：告警",0]
[null,20137,"缺水故障","Bit","0：正常；1：告警",0]
[null,20138,"电极加湿进水阀","Bit","0：关；1：开",0]
[null,20139,"电极加湿排水阀","Bit","0：关；1：开",0]
[null,20140,"湿膜加湿水泵","Bit","0：关；1：开",0]
[null,20141,"湿膜加湿进水阀","Bit","0：关；1：开",0]
[null,20142,"加湿器维护时间到","Bit","0：正常；1：告警",0]
[null,20143,"保留","Bit",null,0]
[null,20144,"加热器1状态","Bit","0：关；1：开",0]
[null,20145,"加热器2状态","Bit","0：关；1：开",0]
[null,20146,"加热器1故障","Bit","0：正常；1：告警",0]
[null,20147,"加热器2故障","Bit","0：正常；1：告警",0]
[null,20148,"加热器1保护","Bit","0：正常；1：告警",0]
[null,20149,"加热器2保护","Bit","0：正常；1：告警",0]
[null,20150,"保留","Bit",null,0]
[null,20151,"保留","Bit",null,0]
[null,20152,"保留","Bit",null,0]
[null,20153,"回风温度1故障","Bit","0：正常；1：告警",0]
[null,20154,"回风温度2故障","Bit","0：正常；1：告警",0]
[null,20155,"回风湿度故障","Bit","0：正常；1：告警",0]
[null,20156,"送风温度1故障","Bit","0：正常；1：告警",0]
[null,20157,"送风温度2故障","Bit","0：正常；1：告警",0]
[null,20158,"送风温度3故障","Bit","0：正常；1：告警",0]
[null,20159,"送风湿度故障","Bit","0：正常；1：告警",0]
[null,20160,"排气温度1故障","Bit","0：正常；1：告警",0]
[null,20161,"吸气温度1故障","Bit","0：正常；1：告警",0]
[null,20162,"吸气压力1故障","Bit","0：正常；1：告警",0]
[null,20163,"排气压力1故障","Bit","0：正常；1：告警",0]
[null,20164,"排气温度2故障","Bit","0：正常；1：告警",0]
[null,20165,"吸气温度2故障","Bit","0：正常；1：告警",0]
[null,20166,"吸气压力2故障","Bit","0：正常；1：告警",0]
[null,20167,"排气压力2故障","Bit","0：正常；1：告警",0]
[null,20168,"风压差传感器故障","Bit","0：正常；1：告警",0]
[null,20169,"液管温度1故障","Bit","0：正常；1：告警",0]
[null,20170,"液管温度2故障","Bit","0：正常；1：告警",0]
[null,20171,"保留","Bit",null,0]
[null,20172,"保留","Bit",null,0]
[null,20173,"保留","Bit",null,0]
[null,20174,"保留","Bit",null,0]
[null,20175,"保留","Bit",null,0]
[null,20176,"保留","Bit",null,0]
[null,20177,"保留","Bit",null,0]
[null,20178,"保留","Bit",null,0]
[null,20179,"远程温湿度1故障","Bit","0：正常；1：告警",0]
[null,20180,"远程温湿度2故障","Bit","0：正常；1：告警",0]
[null,20181,"远程温湿度3故障","Bit","0：正常；1：告警",0]
[null,20182,"远程温湿度4故障","Bit","0：正常；1：告警",0]
[null,20183,"远程温湿度5故障","Bit","0：正常；1：告警",0]
[null,20184,"远程温湿度6故障","Bit","0：正常；1：告警",0]
[null,20185,"远程温湿度7故障","Bit","0：正常；1：告警",0]
[null,20186,"远程温湿度8故障","Bit","0：正常；1：告警",0]
[null,20187,"远程温湿度9故障","Bit","0：正常；1：告警",0]
[null,20188,"远程温湿度10故障","Bit","0：正常；1：告警",0]
[null,20189,"远程温湿度11故障","Bit","0：正常；1：告警",0]
[null,20190,"远程温湿度12故障","Bit","0：正常；1：告警",0]
[null,20191,"远程温湿度13故障","Bit","0：正常；1：告警",0]
[null,20192,"远程温湿度14故障","Bit","0：正常；1：告警",0]
[null,20193,"远程温湿度15故障","Bit","0：正常；1：告警",0]
[null,20194,"远程温湿度16故障","Bit","0：正常；1：告警",0]
[null,20195,"组网通讯故障","Bit","0：正常；1：告警",0]
[null,20196,"组网地址冲突","Bit","0：正常；1：告警",0]
[null,20197,"组网软件不匹配","Bit","0：正常；1：告警",0]
[null,20198,"保留","Bit",null,0]
[null,20199,"保留","Bit",null,0]
[null,20200,"从机00离线","Bit","0：正常；1：告警",0]
[null,20201,"从机01离线","Bit","0：正常；1：告警",0]
[null,20202,"从机02离线","Bit","0：正常；1：告警",0]
[null,20203,"从机03离线","Bit","0：正常；1：告警",0]
[null,20204,"从机04离线","Bit","0：正常；1：告警",0]
[null,20205,"从机05离线","Bit","0：正常；1：告警",0]
[null,20206,"从机06离线","Bit","0：正常；1：告警",0]
[null,20207,"从机07离线","Bit","0：正常；1：告警",0]
[null,20208,"从机08离线","Bit","0：正常；1：告警",0]
[null,20209,"从机09离线","Bit","0：正常；1：告警",0]
[null,20210,"从机10离线","Bit","0：正常；1：告警",0]
[null,20211,"从机11离线","Bit","0：正常；1：告警",0]
[null,20212,"从机12离线","Bit","0：正常；1：告警",0]
[null,20213,"从机13离线","Bit","0：正常；1：告警",0]
[null,20214,"从机14离线","Bit","0：正常；1：告警",0]
[null,20215,"从机15离线","Bit","0：正常；1：告警",0]
[null,20216,"从机16离线","Bit","0：正常；1：告警",0]
[null,20217,"从机17离线","Bit","0：正常；1：告警",0]
[null,20218,"从机18离线","Bit","0：正常；1：告警",0]
[null,20219,"从机19离线","Bit","0：正常；1：告警",0]
[null,20220,"从机20离线","Bit","0：正常；1：告警",0]
[null,20221,"从机21离线","Bit","0：正常；1：告警",0]
[null,20222,"从机22离线","Bit","0：正常；1：告警",0]
[null,20223,"从机23离线","Bit","0：正常；1：告警",0]
[null,20224,"从机24离线","Bit","0：正常；1：告警",0]
[null,20225,"从机25离线","Bit","0：正常；1：告警",0]
[null,20226,"从机26离线","Bit","0：正常；1：告警",0]
[null,20227,"从机27离线","Bit","0：正常；1：告警",0]
[null,20228,"从机28离线","Bit","0：正常；1：告警",0]
[null,20229,"从机29离线","Bit","0：正常；1：告警",0]
[null,20230,"从机30离线","Bit","0：正常；1：告警",0]
[null,20231,"从机31离线","Bit","0：正常；1：告警",0]
[null,20232,"从机32离线","Bit","0：正常；1：告警",0]
[null,20233,"从机33离线","Bit","0：正常；1：告警",0]
[null,20234,"从机34离线","Bit","0：正常；1：告警",0]
[null,20235,"从机35离线","Bit","0：正常；1：告警",0]
[null,20236,"从机36离线","Bit","0：正常；1：告警",0]
[null,20237,"从机37离线","Bit","0：正常；1：告警",0]
[null,20238,"从机38离线","Bit","0：正常；1：告警",0]
[null,20239,"从机39离线","Bit","0：正常；1：告警",0]
[null,20240,"从机40离线","Bit","0：正常；1：告警",0]
[null,20241,"从机41离线","Bit","0：正常；1：告警",0]
[null,20242,"从机42离线","Bit","0：正常；1：告警",0]
[null,20243,"从机43离线","Bit","0：正常；1：告警",0]
[null,20244,"从机44离线","Bit","0：正常；1：告警",0]
[null,20245,"从机45离线","Bit","0：正常；1：告警",0]
[null,20246,"从机46离线","Bit","0：正常；1：告警",0]
[null,20247,"从机47离线","Bit","0：正常；1：告警",0]
[null,20248,"从机48离线","Bit","0：正常；1：告警",0]
[null,20249,"从机49离线","Bit","0：正常；1：告警",0]
[null,20250,"从机50离线","Bit","0：正常；1：告警",0]
[null,20251,"从机51离线","Bit","0：正常；1：告警",0]
[null,20252,"从机52离线","Bit","0：正常；1：告警",0]
[null,20253,"从机53离线","Bit","0：正常；1：告警",0]
[null,20254,"从机54离线","Bit","0：正常；1：告警",0]
[null,20255,"从机55离线","Bit","0：正常；1：告警",0]
[null,20256,"从机56离线","Bit","0：正常；1：告警",0]
[null,20257,"从机57离线","Bit","0：正常；1：告警",0]
[null,20258,"从机58离线","Bit","0：正常；1：告警",0]
[null,20259,"从机59离线","Bit","0：正常；1：告警",0]
[null,20260,"从机60离线","Bit","0：正常；1：告警",0]
[null,20261,"从机61离线","Bit","0：正常；1：告警",0]
[null,20262,"从机62离线","Bit","0：正常；1：告警",0]
[null,20263,"从机63离线","Bit","0：正常；1：告警",0]
[null,20264,"风机1过载","Bit","0：闭合；1：断开",0]
[null,20265,"风机2过载","Bit","0：闭合；1：断开",0]
[null,20266,"风机3过载","Bit","0：闭合；1：断开",0]
[null,20267,"高压开关1","Bit","0：闭合；1：断开",0]
[null,20268,"低压开关1","Bit","0：闭合；1：断开",0]
[null,20269,"高压开关2","Bit","0：闭合；1：断开",0]
[null,20270,"低压开关2","Bit","0：闭合；1：断开",0]
[null,20271,"室外风机过载1","Bit","0：闭合；1：断开",0]
[null,20272,"室外风机过载2","Bit","0：闭合；1：断开",0]
[null,20273,"湿膜低水位","Bit","0：闭合；1：断开",0]
[null,20274,"冷凝高水位","Bit","0：闭合；1：断开",0]
[null,20275,"电加热过载1","Bit","0：闭合；1：断开",0]
[null,20276,"电加热过载2","Bit","0：闭合；1：断开",0]
[null,20277,"气流流失","Bit","0：闭合；1：断开",0]
[null,20278,"滤网堵塞","Bit","0：闭合；1：断开",0]
[null,20279,"烟雾报警","Bit","0：闭合；1：断开",0]
[null,20280,"远程开关","Bit","0：闭合；1：断开",0]
[null,20281,"保留","Bit",null,0]
[null,20282,"保留","Bit",null,0]
[null,20283,"保留","Bit",null,0]
[null,20284,"保留","Bit",null,0]
[null,20285,"保留","Bit",null,0]
[null,20286,"保留","Bit",null,0]
[null,20287,"保留","Bit",null,0]
[null,20288,"保留","Bit",null,0]
[null,20289,"保留","Bit",null,0]

{"sheet":"只读模拟量","index":2,"n_rows":151,"n_cols":7,"rows_kept":151,"merged":[[0,1,0,10]]}
[null,"04功能码读"]
[null,"地址","变量名称","类型","单位","系数","说明"]
[null,40000,"实际控制方式","int16",null,1,"0：回风控制；1：送风控制"]
[null,40001,"当前控制温度","int16","℃",0.1]
[null,40002,"当前控制湿度","int16","%",0.1]
[null,40003,"控制温度设定值","int16","℃",0.1]
[null,40004,"控制湿度设定值","int16","%",0.1]
[null,40005,"室内回风温度","int16","℃",0.1]
[null,40006,"室内回风湿度","int16","%",0.1]
[null,40007,"室内送风温度","int16","℃",0.1]
[null,40008,"室内送风湿度","int16","%",0.1]
[null,40009,"室内回风温度1","int16","℃",0.1]
[null,40010,"室内回风温度2","int16","℃",0.1]
[null,40011,"室内送风温度1","int16","℃",0.1]
[null,40012,"室内送风温度2","int16","℃",0.1]
[null,40013,"室内送风温度3","int16","℃",0.1]
[null,40014,"机组状态","uint16",null,1,"0本地关机；1开机；2故障关机；3群组待机; 4关机中；5远程关机"]
[null,40015,"运行模式","uint16",null,1,"1：制冷模式；2：除湿模式；4：加热模式；6：加热除湿模式；8：加湿模式；9：制冷加湿模式；12：加热加湿模式；16：送风模式"]
[null,40016,"软件版本","uint16",null,1]
[null,40017,"风量","int16","m3/h",1]
[null,40018,"制冷量","int16","kW",0.1]
[null,40019,"制冷需求","int16",null,0.1]
[null,40020,"制热需求","int16",null,0.1]
[null,40021,"加湿需求","int16",null,0.1]
[null,40022,"除湿需求","int16",null,0.1]
[null,40023,"加湿电流","int16","A",0.1]
[null,40024,"高水位电压","int16","V",1]
[null,40025,"A相电压","int16","V",0.1]
[null,40026,"B相电压","int16","V",0.1]
[null,40027,"C相电压","int16","V",0.1]
[null,40028,"A相频率","int16","Hz",0.1]
[null,40029,"B相频率","int16","Hz",1]
[null,40030,"C相频率","int16","Hz",0.1]
[null,40031,"风机转速","int16","%",0.1]
[null,40032,"风压差值","int16","%",0.1]
[null,40033,"外风机转速","int16","%",0.1]
[null,40034,"外风机2转速","int16","%",0.1]
[null,40035,"保留","int16",null,1]
[null,40036,"保留","int16",null,1]
[null,40037,"保留","uint16",null,1]
[null,40038,"保留","int16",null,1]
[null,40039,"保留","int16",null,1]
[null,40040,"保留","int16",null,1]
[null,40041,"保留","int16",null,1]
[null,40042,"保留","int16",null,1]
[null,40043,"保留","int16",null,1]
[null,40044,"排气温度1","int16","℃",0.1]
[null,40045,"吸气温度1","int16","℃",0.1]
[null,40046,"蒸发温度1","int16","℃",0.1]
[null,40047,"吸气压力1","int16","Bar",0.1]
[null,40048,"排气压力1","int16","Bar",0.1]
[null,40049,"冷凝温度1","int16","℃",0.1]
[null,40050,"吸气过热度1","int16",null,0.1]
[null,40051,"EEV1开度","int16",null,1]
[null,40052,"保护调节高压值1","int16","Bar",0.1]
[null,40053,"压缩机1运行频率","int16","Hz",0.1]
[null,40054,"压缩机1设置频率","int16","Hz",0.1]
[null,40055,"压缩机1保护调节码","int16",null,1]
[null,40056,"变频器1母线电压","int16","V",0.1]
[null,40057,"变频器1输出电压","int16","V",0.1]
[null,40058,"变频器1输出电流","int16","A",0.1]
[null,40059,"逆变模块1温度","int16","℃",0.1]
[null,40060,"变频器1软件版本","int16",null,1]
[null,40061,"变频器1故障码","int16",null,1]
[null,40062,"变频器1状态","int16",null,1]
[null,40063,"液管温度1","int16","℃",0.1]
[null,40064,"保留","int16",null,1]
[null,40065,"保留","int16",null,1]
[null,40066,"保留","int16",null,1]
[null,40067,"保留","int16",null,1]
[null,40068,"保留","int16",null,1]
[null,40069,"保留","int16",null,1]
[null,40070,"保留","int16",null,1]
[null,40071,"保留","int16",null,1]
[null,40072,"保留","int16",null,1]
[null,40073,"排气温度2","int16","℃",0.1]
[null,40074,"吸气温度2","int16","℃",0.1]
[null,40075,"蒸发温度2","int16","℃",0.1]
[null,40076,"吸气压力2","int16","Bar",0.1]
[null,40077,"排气压力2","int16","Bar",0.1]
[null,40078,"冷凝温度2","int16","℃",0.1]
[null,40079,"吸气过热度2","int16",null,0.1]
[null,40080,"EEV2开度","int16",null,1]
[null,40081,"保护调节高压值2","int16","Bar",0.1]
[null,40082,"压缩机2运行频率","int16","Hz",0.1]
[null,40083,"压缩机2设置频率","int16","Hz",0.1]
[null,40084,"压缩机2保护调节码","int16",null,1]
[null,40085,"变频器2母线电压","int16","V",0.1]
[null,40086,"变频器2输出电压","int16","V",0.1]
[null,40087,"变频器2输出电流","int16","A",0.1]
[null,40088,"逆变模块2温度","int16","℃",0.1]
[null,40089,"变频器2软件版本","int16",null,1]
[null,40090,"变频器2故障码","int16",null,1]
[null,40091,"变频器2状态","int16",null,1]
[null,40092,"液管温度2","int16","℃",0.1]
[null,40093,"保留","int16",null,1]
[null,40094,"保留","int16",null,1]
[null,40095,"保留","int16",null,1]
[null,40096,"保留","int16",null,1]
[null,40097,"保留","int16",null,1]
[null,40098,"保留","int16",null,1]
[null,40099,"保留","int16",null,1]
[null,40100,"保留","int16",null,1]
[null,40101,"保留","int16",null,1]
[null,40102,"机组运行时间","int16","H",1]
[null,40103,"内风机运行时间","int16","H",1]
[null,40104,"加湿器运行时间","int16","H",1]
[null,40105,"加热器1运行时间","int16","H",1]
[null,40106,"加热器2运行时间","int16","H",1]
[null,40107,"外风机运行时间","int16","H",1]
[null,40108,"压缩机1运行时间","int16","H",1]
[null,40109,"压缩机2运行时间","int16","H",1]
[null,40110,"滤网运行时间","int16","H",1]
[null,40111,"冷凝水泵运行时间","int16","H",1]
[null,40112,"外风机2运行时间","int16","H",1]
[null,40113,"保留","int16"]
[null,40114,"保留","int16"]
[null,40115,"保留","int16"]
[null,40116,"保留","int16"]
[null,40117,"远程温度01","int16","℃",0.1]
[null,40118,"远程湿度01","int16","%",0.1]
[null,40119,"远程温度02","int16","℃",0.1]
[null,40120,"远程湿度02","int16","%",0.1]
[null,40121,"远程温度03","int16","℃",0.1]
[null,40122,"远程湿度03","int16","%",0.1]
[null,40123,"远程温度04","int16","℃",0.1]
[null,40124,"远程湿度04","int16","%",0.1]
[null,40125,"远程温度05","int16","℃",0.1]
[null,40126,"远程湿度05","int16","%",0.1]
[null,40127,"远程温度06","int16","℃",0.1]
[null,40128,"远程湿度06","int16","%",0.1]
[null,40129,"远程温度07","int16","℃",0.1]
[null,40130,"远程湿度07","int16","%",0.1]
[null,40131,"远程温度08","int16","℃",0.1]
[null,40132,"远程湿度08","int16","%",0.1]
[null,40133,"远程温度09","int16","℃",0.1]
[null,40134,"远程湿度09","int16","%",0.1]
[null,40135,"远程温度10","int16","℃",0.1]
[null,40136,"远程湿度10","int16","%",0.1]
[null,40137,"远程温度11","int16","℃",0.1]
[null,40138,"远程湿度11","int16","%",0.1]
[null,40139,"远程温度12","int16","℃",0.1]
[null,40140,"远程湿度12","int16","%",0.1]
[null,40141,"远程温度13","int16","℃",0.1]
[null,40142,"远程湿度13","int16","%",0.1]
[null,40143,"远程温度14","int16","℃",0.1]
[null,40144,"远程湿度14","int16","%",0.1]
[null,40145,"远程温度15","int16","℃",0.1]
[null,40146,"远程湿度15","int16","%",0.1]
[null,40147,"远程温度16","int16","℃",0.1]
[null,40148,"远程湿度16","int16","%",0.1]

{"sheet":"读写模拟量","index":3,"n_rows":509,"n_cols":11,"rows_kept":509,"merged":[[0,1,0,10]]}
[null,"03功能码读；06功能码写；"]
[null,"地址","变量名称","类型","单位","系数","最大值","最小值","默认值","是否保存","说明"]
[null,30000,"开关机控制","uint16",null,1,32767,-32768,0,true,"0x0000关机，0xFF00开机"]
[null,30001,"送风温度设定","int16","℃",0.1,450,150,220,true]
[null,30002,"回风温度设定","int16","℃",0.1,450,180,300,true]
[null,30003,"温度控制方式","int16",null,1,1,0,0,true,"0：回风温度控制1：送风温度控制"]
[null,30004,"湿度设定","int16","%",0.1,950,100,400,true]
[null,30005,"来电自启延时","int16","S",1,240,0,6,true]
[null,30006,"来电自启使能","uint16",null,1,32767,-32768,-256,true,"0x0000：禁止；0xFF00：使能"]
[null,30007,"保留","uint16",null,1,0,0,0,false]
[null,30008,"故障复位","uint16",null,1,32767,-32768,0,false]
[null,30009,"制冷比例带","int16","℃",0.1,50,10,15,true]
[null,30010,"制热比例带","int16","℃",0.1,50,10,30,true]
[null,30011,"加湿比例带","int16","%",0.1,200,10,50,true]
[null,30012,"除湿比例带","int16","%",0.1,200,10,50,true]
[null,30013,"温度控制死区","int16","℃",0.1,50,0,5,true]
[null,30014,"湿度控制死区","int16","%",0.1,200,10,10,true]
[null,30015,"年","int16",null,1,255,0,0,false,"实际值等于2000+设置值;"]
[null,30016,"月","int16",null,1,12,1,1,false]
[null,30017,"日","int16",null,1,31,1,1,false]
[null,30018,"时","int16",null,1,23,0,0,false]
[null,30019,"分","int16",null,1,59,0,0,false]
[null,30020,"秒","int16",null,1,59,0,0,false]
[null,30021,"Modbus地址","int16",null,1,240,1,1,true]
[null,30022,"Modbus波特率","int16",null,1,3,0,2,true,"0：2400；1：4800；2：9600；3：19200"]
[null,30023,"组网使能","uint16",null,1,32767,-32768,0,true,"0x0000：禁止；0xFF00：使能"]
[null,30024,"组网地址","int16",null,1,63,0,0,true]
[null,30025,"组网数量","int16",null,1,64,2,2,true]
[null,30026,"切换数量","int16",null,1,64,1,1,true,"每次切换的数量"]
[null,30027,"轮值周期","int16","H",1,240,0,24,true]
[null,30028,"运行数量","int16",null,1,63,1,1,true,"同时运行的数量"]
[null,30029,"需求同步","uint16",null,1,32767,-32768,0,true,"0x0000：禁止；0xFF00：使能"]
[null,30030,"层叠功能","uint16",null,1,32767,-32768,0,true,"0x0000：禁止；0xFF00：使能"]
[null,30031,"高温同开","uint16",null,1,32767,-32768,0,false,"0x0000：禁止；0xFF00：使能"]
[null,30032,"远程开关机禁止","uint16",null,1,32767,-32768,0,true,"0x0000：远程开机使能；0xFF00：远程开机禁止"]
[null,30033,"保留","int16",null,1,0,0,0,false]
[null,30034,"保留","int16",null,1,0,0,0,false]
[null,30035,"保留","int16",null,1,0,0,0,false]
[null,30036,"定时开关机使能","uint16",null,1,32767,-32768,0,true,"0x0000：禁止；0xA0A0：使能"]
[null,30037,"周日开机时间","int16","Min",1,1440,0,0,true]
[null,30038,"周一开机时间","int16","Min",1,1440,0,0,true]
[null,30039,"周二开机时间","int16","Min",1,1440,0,0,true]
[null,30040,"周三开机时间","int16","Min",1,1440,0,0,true]
[null,30041,"周四开机时间","int16","Min",1,1440,0,0,true]
[null,30042,"周五开机时间","int16","Min",1,1440,0,0,true]
[null,30043,"周六开机时间","int16","Min",1,1440,0,0,true]
[null,30044,"周日关机时间","int16","Min",1,1440,0,0,true]
[null,30045,"周一关机时间","int16","Min",1,1440,0,0,true]
[null,30046,"周二关机时间","int16","Min",1,1440,0,0,true]
[null,30047,"周三关机时间","int16","Min",1,1440,0,0,true]
[null,30048,"周四关机时间","int16","Min",1,1440,0,0,true]
[null,30049,"周五关机时间","int16","Min",1,1440,0,0,true]
[null,30050,"周六关机时间","int16","Min",1,1440,0,0,true]
[null,30051,"保留","int16",null,1,0,0,0,false]
[null,30052,"保留","int16",null,1,0,0,0,false]
[null,30053,"保留","int16",null,1,0,0,0,false]
[null,30054,"保留","int16",null,1,0,0,0,false]
[null,30055,"保留","int16",null,1,0,0,0,false]
[null,30056,"保留","int16",null,1,0,0,0,false]
[null,30057,"保留","int16",null,1,0,0,0,false]
[null,30058,"保留","int16",null,1,0,0,0,false]
[null,30059,"保留","int16",null,1,0,0,0,false]
[null,30060,"保留","int16",null,1,0,0,0,false]
[null,30061,"保留","int16",null,1,0,0,0,false]
[null,30062,"保留","int16",null,1,0,0,0,false]
[null,30063,"保留","int16",null,1,0,0,0,false]
[null,30064,"保留","int16",null,1,0,0,0,false]
[null,30065,"保留","int16",null,1,0,0,0,false]
[null,30066,"保留","int16",null,1,0,0,0,false]
[null,30067,"保留","int16",null,1,0,0,0,false]
[null,30068,"保留","int16",null,1,0,0,0,false]
[null,30069,"保留","int16",null,1,0,0,0,false]
[null,30070,"抽真空使能","int16",null,1,32767,-32768,0,false,"0x0000：禁止；0xA0A0：使能"]
[null,30071,"手动使能","int16",null,1,32767,-32768,0,false,"0x0000：禁止；0xA0A0：使能"]
[null,30072,"内风机1开关","int16",null,1,1,0,0,false]
[null,30073,"内风机2开关","int16",null,1,1,0,0,false]
[null,30074,"内风机3开关","int16",null,1,1,0,0,false]
[null,30075,"内风机转速","int16","%",0.1,1000,0,0,false]
[null,30076,"外风机1开关","int16",null,1,1,0,0,false]
[null,30077,"外风机2开关","int16",null,1,1,0,0,false]
[null,30078,"外风机转速","int16","%",0.1,1000,0,0,false]
[null,30079,"电加热1开关","int16",null,1,1,0,0,false]
[null,30080,"电加热1开关","int16",null,1,1,0,0,false]
[null,30081,"加湿器开关","int16",null,1,1,0,0,false]
[null,30082,"电极加湿进水阀","int16",null,1,1,0,0,false]
[null,30083,"电极加湿排水阀","int16",null,1,1,0,0,false]
[null,30084,"湿膜加湿进水阀","int16",null,1,1,0,0,false]
[null,30085,"湿膜加湿水泵开关","uint16",null,1,1,0,0,false]
[null,30086,"冷凝水泵开关","uint16",null,1,1,0,0,false]
[null,30087,"液管电磁阀1","uint16",null,1,1,0,0,false]
[null,30088,"液管电磁阀2","uint16",null,1,1,0,0,false]
[null,30089,"压缩机1加热开关","uint16",null,1,1,0,0,false]
[null,30090,"压缩机2加热开关","uint16",null,1,1,0,0,false]
[null,30091,"压缩机1开关","uint16",null,1,1,0,0,false]
[null,30092,"压缩机2开关","uint16",null,1,1,0,0,false]
[null,30093,"压缩机1频率","uint16","Hz",0.1,1200,0,0,false]
[null,30094,"压缩机2频率","uint16","Hz",0.1,1200,0,0,false]
[null,30095,"EEV1开度","uint16",null,1,480,0,0,false]
[null,30096,"EEV2开度","uint16",null,1,480,0,0,false]
[null,30097,"调试时间","uint16","Min",1,999,1,60,false]
[null,30098,"外风机2转速","uint16","%",0.1,1000,0,0,false]
[null,30099,"保留","uint16",null,1,0,0,0,false]
[null,30100,"保留","uint16",null,1,0,0,0,false]
[null,30101,"保留","uint16",null,1,0,0,0,false]
[null,30102,"保留","int16",null,1,0,0,0,false]
[null,30103,"保留","int16",null,1,0,0,0,false]
[null,30104,"保留","int16",null,1,0,0,0,false]
[null,30105,"保留","int16",null,1,0,0,0,false]
[null,30106,"保留","int16",null,1,0,0,0,false]
[null,30107,"保留","int16",null,1,0,0,0,false]
[null,30108,"保留","int16",null,1,0,0,0,false]
[null,30109,"保留","int16",null,1,0,0,0,false]
[null,30110,"保留","int16",null,1,0,0,0,false]
[null,30111,"保留","int16",null,1,0,0,0,false]
[null,30112,"保留","int16",null,1,0,0,0,false]
[null,30113,"风量修正","int16",null,0.01,500,0,0,true]
[null,30114,"制冷量修正","int16",null,0.01,500,0,0,true]
[null,30115,"回风温度1修正","int16","℃",0.1,99,-99,0,true]
[null,30116,"回风温度2修正","int16","℃",0.1,99,-99,0,true]
[null,30117,"送风温度1修正","int16","℃",0.1,99,-99,0,true]
[null,30118,"送风温度2修正","int16","℃",0.1,99,-99,0,true]
[null,30119,"送风温度3修正","int16","℃",0.1,99,-99,0,true]
[null,30120,"回风湿度修正","int16","%",0.1,300,-300,0,true]
[null,30121,"送风湿度修正","int16","%",0.1,300,-300,0,true]
[null,30122,"吸气温度1修正","int16","℃",0.1,99,-99,0,true]
[null,30123,"排气温度1修正","int16","℃",0.1,99,-99,0,true]
[null,30124,"吸气压力1修正","int16","bar",0.1,99,-99,0,true]
[null,30125,"排气压力1修正","int16","bar",0.1,99,-99,0,true]
[null,30126,"吸气温度2修正","int16","℃",0.1,99,-99,0,true]
[null,30127,"排气温度2修正","int16","℃",0.1,99,-99,0,true]
[null,30128,"吸气压力2修正","int16","bar",0.1,99,-99,0,true]
[null,30129,"排气压力2修正","int16","bar",0.1,99,-99,0,true]
[null,30130,"风压差修正","int16","Pa",0.1,300,-300,0,true]
[null,30131,"加湿电流修正","int16","A",0.1,99,-99,0,true]
[null,30132,"远程温度01修正","int16","℃",0.1,99,-99,0,true]
[null,30133,"远程温度02修正","int16","℃",0.1,99,-99,0,true]
[null,30134,"远程温度03修正","int16","℃",0.1,99,-99,0,true]
[null,30135,"远程温度04修正","int16","℃",0.1,99,-99,0,true]
[null,30136,"远程温度05修正","int16","℃",0.1,99,-99,0,true]
[null,30137,"远程温度06修正","int16","℃",0.1,99,-99,0,true]
[null,30138,"远程温度07修正","int16","℃",0.1,99,-99,0,true]
[null,30139,"远程温度08修正","int16","℃",0.1,99,-99,0,true]
[null,30140,"远程温度09修正","int16","℃",0.1,99,-99,0,true]
[null,30141,"远程温度10修正","int16","℃",0.1,99,-99,0,true]
[null,30142,"远程温度11修正","int16","℃",0.1,99,-99,0,true]
[null,30143,"远程温度12修正","int16","℃",0.1,99,-99,0,true]
[null,30144,"远程温度13修正","int16","℃",0.1,99,-99,0,true]
[null,30145,"远程温度14修正","int16","℃",0.1,99,-99,0,true]
[null,30146,"远程温度15修正","int16","℃",0.1,99,-99,0,true]
[null,30147,"远程温度16修正","int16","℃",0.1,99,-99,0,true]
[null,30148,"远程湿度01修正","int16","%",0.1,300,-300,0,true]
[null,30149,"远程湿度02修正","int16","%",0.1,300,-300,0,true]
[null,30150,"远程湿度03修正","int16","%",0.1,300,-300,0,true]
[null,30151,"远程湿度04修正","int16","%",0.1,300,-300,0,true]
[null,30152,"远程湿度05修正","int16","%",0.1,300,-300,0,true]
[null,30153,"远程湿度06修正","int16","%",0.1,300,-300,0,true]
[null,30154,"远程湿度07修正","int16","%",0.1,300,-300,0,true]
[null,30155,"远程湿度08修正","int16","%",0.1,300,-300,0,true]
[null,30156,"远程湿度09修正","int16","%",0.1,300,-300,0,true]
[null,30157,"远程湿度10修正","int16","%",0.1,300,-300,0,true]
[null,30158,"远程湿度11修正","int16","%",0.1,300,-300,0,true]
[null,30159,"远程湿度12修正","int16","%",0.1,300,-300,0,true]
[null,30160,"远程湿度13修正","uint16","%",0.1,300,-300,0,true]
[null,30161,"远程湿度14修正","uint16","%",0.1,300,-300,0,true]
[null,30162,"远程湿度15修正","uint16","%",0.1,300,-300,0,true]
[null,30163,"远程湿度16修正","uint16","%",0.1,300,-300,0,true]
[null,30164,"保留","uint16",null,1,0,0,0,false]
[null,30165,"保留","uint16",null,1,0,0,0,false]
[null,30166,"保留","uint16",null,1,0,0,0,false]
[null,30167,"保留","uint16",null,1,0,0,0,false]
[null,30168,"保留","uint16",null,1,0,0,0,false]
[null,30169,"保留","uint16",null,1,0,0,0,false]
[null,30170,"保留","uint16",null,1,0,0,0,false]
[null,30171,"保留","int16",null,1,0,0,0,false]
[null,30172,"保留","int16",null,1,0,0,0,false]
[null,30173,"保留","int16",null,1,0,0,0,false]
[null,30174,"保留","int16",null,1,0,0,0,false]
[null,30175,"保留","int16",null,1,0,0,0,false]
[null,30176,"保留","int16",null,1,0,0,0,false]
[null,30177,"保留","int16",null,1,0,0,0,false]
[null,30178,"机组运行时间","int16","H",1,32767,-32768,0,false]
[null,30179,"风机运行时间","int16","H",1,32767,-32768,0,false]
[null,30180,"外风机1运行时间","int16","H",1,32767,-32768,0,false]
[null,30181,"压缩机1运行时间","int16","H",1,32767,-32768,0,false]
[null,30182,"压缩机2运行时间","int16","H",1,32767,-32768,0,false]
[null,30183,"加湿运行时间","int16","H",1,32767,-32768,0,false]
[null,30184,"加热器1运行时间","int16","H",1,32767,-32768,0,false]
[null,30185,"加热器2运行时间","int16","H",1,32767,-32768,0,false]
[null,30186,"滤网运行时间","int16","H",1,32767,-32768,0,false]
[null,30187,"冷凝水泵运行时间","int16","H",1,32767,-32768,0,false]
[null,30188,"外风机2运行时间","int16","H",1,32767,-32768,0,false]
[null,30189,"保留","int16",null,1,0,0,0,false]
[null,30190,"保留","int16",null,1,0,0,0,false]
[null,30191,"保留","int16",null,1,0,0,0,false]
[null,30192,"保留","int16",null,1,0,0,0,false]
[null,30193,"保留","int16",null,1,0,0,0,false]
[null,30194,"保留","int16",null,1,0,0,0,false]
[null,30195,"保留","int16",null,1,0,0,0,false]
[null,30196,"保留","int16",null,1,0,0,0,false]
[null,30197,"保留","int16",null,1,0,0,0,false]
[null,30198,"空调型号","int16",null,1,2,0,0,true]
[null,30199,"制冷剂类型","int16",null,1,1,0,0,true,"0：R410A"]
[null,30200,"温度计算方式","int16",null,1,1,0,0,true,"0:平均温度；1：最高温度"]
[null,30201,"风机控制方式","int16",null,1,1,0,0,true,"0：温度控制；1：压差控制"]
[null,30202,"需求控制周期","int16","S",1,100,1,2,true]
[null,30203,"保护调节周期","int16","S",1,100,1,5,true]
[null,30204,"滤网维护时间","int16","H",1,32767,0,4000,true,"0不告警"]
[null,30205,"压差控制设定值","int16","Pa",0.1,500,5,50,true]
[null,30206,"除湿压差系数","int16",null,0.1,900,500,700,true]
[null,30207,"压差控制偏差","int16",null,0.1,300,10,100,true]
[null,30208,"冷凝水泵运行时间","int16","s",1,999,1,5,true]
[null,30209,"湿膜水阀开启时间","int16","s",1,240,1,10,true]
[null,30210,"湿膜水阀关闭时间","int16","s",1,240,1,180,true]
[null,30211,"除湿低温限制","int16","℃",0.1,100,0,40,true]
[null,30212,"风量显示使能","uint16",null,1,32767,-32768,-24159,true,"0xA1A1使能，其他值无效"]
[null,30213,"制冷量显示使能","uint16",null,1,32767,-32768,-24159,true,"0xA1A1使能，其他值无效"]
[null,30214,"制冷加湿使能","uint16",null,1,32767,-32768,-24159,true,"0xA1A1使能，其他值无效"]
[null,30215,"除湿控制使能","uint16",null,1,32767,-32768,-24159,true,"0xA1A1使能，其他值无效"]
[null,30216,"设备使能1","int16",null,1,32767,-32768,"0x0035",true]
[null,30217,"设备使能2","int16",null,1,32767,-32768,0,true]
[null,30218,"设备使能3","int16",null,1,32767,-32768,0,true]
[null,30219,"回风高温告警值","int16","℃",0.1,500,200,400,true]
[null,30220,"回风低温告警值","int16","℃",0.1,300,0,100,true]
[null,30221,"送风高温告警值","int16","℃",0.1,500,200,400,true]
[null,30222,"送风低温告警值","int16","℃",0.1,300,0,100,true]
[null,30223,"高湿告警值","int16","%",0.1,950,100,850,true]
[null,30224,"低湿告警值","int16","%",0.1,950,100,200,true,"Bit0-7：压缩机类型；Bit8-15：风机类型；"]
[null,30225,"漏水报警值","int16",null,1,4096,0,1500,true]
[null,30226,"保留","int16",null,1,0,0,0,false]
[null,30227,"保留","int16",null,1,0,0,0,false,"0：R410A"]
[null,30228,"保留","int16",null,1,0,0,0,false,"0：平均温度；1：最高温度"]
[null,30229,"保留","int16",null,1,0,0,0,false,"0：温度控制；1：压差控制"]
[null,30230,"保留","int16",null,1,0,0,0,false]
[null,30231,"保留","int16",null,1,0,0,0,false]
[null,30232,"保留","int16",null,1,0,0,0,false]
[null,30233,"保留","int16",null,1,0,0,0,false]
[null,30234,"保留","int16",null,1,0,0,0,false]
[null,30235,"保留","int16",null,1,0,0,0,false]
[null,30236,"压缩机型号","int16",null,1,10,0,0,true]
[null,30237,"压缩机数量","int16",null,1,2,1,1,true]
[null,30238,"变频器协议","int16",null,1,2,0,2,true,"0:定频；1：GD（invt）；2：CA（汇川）"]
[null,30239,"轻载制冷使能","int16",null,1,32767,-32768,0,true,"0xA1A1使能，其他值无效"]
[null,30240,"变频器加速时间","uint16","s",1,3600,0,100,true]
[null,30241,"变频器减速时间","uint16","s",1,3600,0,100,true]
[null,30242,"变频器最大频率","uint16","Hz",0.1,1200,0,1000,true]
[null,30243,"变频器下限频率","uint16","Hz",0.1,1200,0,150,true]
[null,30244,"变频器上限频率","uint16","Hz",0.1,1200,0,900,true]
[null,30245,"压缩机最短运行时间","uint16","Min",1,600,1,300,true]
[null,30246,"压缩机最短停止时间","uint16","Min",1,600,1,180,true]
[null,30247,"压缩机启动保持时间","int16","s",1,360,0,120,true]
[null,30248,"制冷模式进入需求","int16",null,0.1,3000,0,1000,true]
[null,30249,"制冷压机停机需求","int16",null,0.1,0,-3000,-1000,true]
[null,30250,"制冷进入除湿需求","int16",null,0.1,1000,0,800,true]
[null,30251,"压缩机额定频率","int16","Hz",0.1,1300,500,900,true]
[null,30252,"压缩机最低频率","int16","Hz",0.1,600,150,200,true]
[null,30253,"压缩机启动台阶频率","int16","Hz",0.1,400,150,300,true]
[null,30254,"压缩机启动保持频率","int16","Hz",0.1,990,400,450,true]
[null,30255,"压缩机降频保护频率","uint16","Hz",0.1,600,250,300,true]
[null,30256,"压缩机回油频率","int16","Hz",0.1,700,400,600,true]
[null,30257,"压缩机回油风险频率","int16","Hz",0.1,700,200,450,true]
[null,30258,"压缩机强制回油时间","int16","Min",1,600,30,180,true]
[null,30259,"压缩机控制周期","int16","Min",1,60,1,4,true]
[null,30260,"回风压缩机比例系数","int16",null,0.1,5000,1,1000,true]
[null,30261,"回风压缩机积分时间","int16",null,0.1,1000,1,100,true]
[null,30262,"送风压缩机比例系数","int16",null,0.1,1000,0,40,true]
[null,30263,"送风压缩机积分时间","int16",null,0.1,100,0,40,true]
[null,30264,"压机关闭特征时间1","int16","Min",1,60,2,5,true]
[null,30265,"压机关闭特征时间2","int16","Min",1,60,2,10,true]
[null,30266,"高压报警值","int16","bar",0.1,500,200,400,true]
[null,30267,"低压报警值","int16","bar",0.1,400,0,40,true]
[null,30268,"吸气低压保护值","int16","bar",0.1,100,10,65,true]
[null,30269,"压缩机低压保护延时","int16","s",1,360,60,180,true]
[null,30270,"排气高温保护值","int16","bar",0.1,1300,700,950,true]
[null,30271,"排气高温告警值","int16","bar",0.1,1300,700,1150,true]
[null,30272,"逆变模块保护温度","int16","℃",0.1,1100,500,1000,true]
[null,30273,"变频器保护电流","int16","A",0.1,500,10,170,true]
[null,30274,"保护调节高压值Pc1","int16",null,0.1,500,100,320,true]
[null,30275,"保护调节高压值Pc2","int16",null,0.1,500,100,350,true]
[null,30276,"保护调节高压值Pc3","int16",null,0.1,500,100,350,true]
[null,30277,"保护调节高压值Pc4","int16",null,0.1,500,100,370,true]
[null,30278,"保护调节高压值Pc5","int16",null,0.1,500,100,350,true]
[null,30279,"压差倍数","int16",null,0.1,30,10,15,true]
[null,30280,"压缩机特征转速Nc1","int16",null,0.1,1300,150,200,true]
[null,30281,"压缩机特征转速Nc2","int16",null,0.1,1300,150,300,true]
[null,30282,"压缩机特征转速Nc3","int16",null,0.1,1300,150,400,true]
[null,30283,"压缩机特征转速Nc4","int16",null,0.1,1300,150,600,true]
[null,30284,"压缩机特征转速Nc5","int16",null,0.1,1300,150,800,true]
[null,30285,"压缩机特征转速Nc6","int16",null,0.1,1300,150,1000,true]
[null,30286,"压缩机共振点1上限","int16",null,0.1,1000,0,0,true]
[null,30287,"压缩机共振点1下限","int16",null,0.1,1000,0,0,true]
[null,30288,"压缩机共振点2上限","int16",null,0.1,1000,0,0,true]
[null,30289,"压缩机共振点2下限","int16",null,0.1,1000,0,0,true]
[null,30290,"压缩机共振点3上限","int16",null,0.1,1000,0,0,true]
[null,30291,"压缩机共振点3下限","int16",null,0.1,1000,0,0,true]
[null,30292,"压缩机共振点4上限","int16",null,0.1,1000,0,0,true]
[null,30293,"压缩机共振点4下限","int16",null,0.1,1000,0,0,true]
[null,30294,"压缩机共振点5上限","int16",null,0.1,1000,0,0,true]
[null,30295,"压缩机共振点5下限","int16",null,0.1,1000,0,0,true]
[null,30296,"制冷单机运行最大负载","int16",null,1,100,0,80,true]
[null,30297,"制冷双机运行最小负载","int16",null,1,100,0,60,true]
[null,30298,"除湿单机运行最大负载","int16",null,1,100,0,80,true]
[null,30299,"除湿双机运行最小负载","int16",null,1,100,0,60,true]
[null,30300,"压缩机除湿最低频率","int16",null,0.1,1000,200,450,true]
[null,30301,"目标频率低关机延时","int16",null,0.1,1000,10,60,true]
[null,30302,"保留","int16",null,1,0,0,0,false]
[null,30303,"保留","int16",null,1,0,0,0,false]
[null,30304,"保留","int16",null,1,0,0,0,false]
[null,30305,"保留","int16",null,1,0,0,0,false]
[null,30306,"保留","int16",null,1,0,0,0,false]
[null,30307,"保留","int16",null,1,0,0,0,false]
[null,30308,"保留","int16",null,1,0,0,0,false]
[null,30309,"保留","int16",null,1,0,0,0,false]
[null,30310,"保留","int16",null,1,0,0,0,false]
[null,30311,"保留","int16",null,1,0,0,0,false]
[null,30312,"保留","int16",null,1,0,0,0,false]
[null,30313,"保留","int16",null,1,0,0,0,false]
[null,30314,"保留","int16",null,1,0,0,0,false]
[null,30315,"保留","int16",null,1,0,0,0,false]
[null,30316,"保留","int16",null,1,0,0,0,false]
[null,30317,"保留","int16",null,1,0,0,0,false]
[null,30318,"保留","int16",null,1,0,0,0,false]
[null,30319,"保留","int16",null,1,0,0,0,false]
[null,30320,"保留","int16",null,1,0,0,0,false]
[null,30321,"保留","int16",null,1,0,0,0,false]
[null,30322,"保留","int16",null,1,0,0,0,false]
[null,30323,"保留","int16",null,1,0,0,0,false]
[null,30324,"保留","int16",null,1,0,0,0,false]
[null,30325,"保留","int16",null,1,0,0,0,false]
[null,30326,"保留","int16",null,1,0,0,0,false]
[null,30327,"保留","int16",null,1,0,0,0,false]
[null,30328,"保留","int16",null,1,0,0,0,false]
[null,30329,"风机型号","int16",null,1,5,0,0,true]
[null,30330,"内风机数量","int16",null,1,16,1,2,true]
[null,30331,"内风机组数","int16",null,1,3,1,3,true]
[null,30332,"风机启动百分比","int16","%",0.1,1000,500,800,true]
[null,30333,"内风机额定转速","int16","%",0.1,1000,10,800,true]
[null,30334,"内风机最低转速","int16","%",0.1,1000,10,400,true]
[null,30335,"开机风机延时","int16",null,1,255,1,3,true]
[null,30336,"内风机控制周期","int16",null,1,60,1,3,true]
[null,30337,"内风机比例系数","int16",null,0.1,1000,1,200,true]
[null,30338,"内风机积分时间","int16",null,0.1,500,1,30,true]
[null,30339,"除湿转速","int16","%",0.1,1000,0,600,true]
[null,30340,"保留","int16",null,1,0,0,0,false]
[null,30341,"保留","int16",null,1,0,0,0,false]
[null,30342,"保留","int16",null,1,0,0,0,false]
[null,30343,"保留","int16",null,1,0,0,0,false]
[null,30344,"保留","int16",null,1,0,0,0,false]
[null,30345,"保留","int16",null,1,0,0,0,false]
[null,30346,"保留","int16",null,1,0,0,0,false]
[null,30347,"保留","int16",null,1,0,0,0,false]
[null,30348,"保留","int16",null,1,0,0,0,false]
[null,30349,"EEV最大开度","int16",null,1,480,0,480,true]
[null,30350,"EEV最小开度","int16",null,1,480,0,20,true]
[null,30351,"EEV初始开度","int16",null,1,320,120,120,true]
[null,30352,"EEV平衡开度","int16",null,1,480,200,300,true]
[null,30353,"EEV平衡时间","int16",null,1,120,0,15,true]
[null,30354,"EEV初始时间","int16",null,1,300,0,20,true]
[null,30355,"EEV平衡压差设置值","int16",null,0.1,200,1,40,true]
[null,30356,"EEV调节周期","int16",null,1,500,1,1,true]
[null,30357,"EEV比例系数","int16",null,0.1,200,1,40,true]
[null,30358,"EEV积分时间","int16",null,0.1,500,1,60,true]
[null,30359,"MOP设定","int16",null,0.1,250,90,150,true]
[null,30360,"MOP比例系数","int16",null,0.1,200,1,40,true]
[null,30361,"MOP积分时间","int16",null,0.1,500,1,60,true]
[null,30362,"制冷吸气过热度","int16",null,0.1,200,50,120,true]
[null,30363,"除湿吸气过热度","int16",null,0.1,200,50,150,true]
[null,30364,"平衡压差使能","int16",null,1,32767,-32768,0,true,"0xA1A1使能，其他值无效"]
[null,30365,"保留","int16",null,1,0,0,0,false]
[null,30366,"保留","uint16",null,1,0,0,0,false]
[null,30367,"保留","int16",null,1,0,0,0,false]
[null,30368,"保留","int16",null,1,0,0,0,false]
[null,30369,"保留","int16",null,1,0,0,0,false]
[null,30370,"冷凝风机控制方式","int16",null,1,2,0,2,true,"0：禁用；1：启停；2：斩波"]
[null,30371,"冷凝风机设置压力","int16",null,0.1,1000,-1000,245,true]
[null,30372,"冷凝风机压力回差","int16",null,0.1,1000,-1000,10,true]
[null,30373,"冷凝风机压力比例","int16",null,0.1,1000,-1000,287,true]
[null,30374,"冷凝风机最小速率","uint16",null,0.1,1000,0,400,true]
[null,30375,"保留","uint16",null,1,0,0,0,false]
[null,30376,"保留","int16",null,1,0,0,0,false]
[null,30377,"保留","int16",null,1,0,0,0,false]
[null,30378,"保留","int16",null,1,0,0,0,false]
[null,30379,"保留","int16",null,1,0,0,0,false]
[null,30380,"加湿器类型","int16",null,1,2,0,2,true]
[null,30381,"加湿器公斤数","int16",null,0.1,250,15,30,true]
[null,30382,"加湿器电压","int16",null,1,480,80,380,true]
[null,30383,"加湿器相数","int16",null,1,3,1,3,true]
[null,30384,"预热电流比","int16",null,1,100,10,20,true]
[null,30385,"预热时间","int16",null,1,999,10,600,true]
[null,30386,"注水电流比","int16",null,1,150,50,80,true]
[null,30387,"停止注水电流比","int16",null,1,150,50,100,true]
[null,30388,"排水电流比","int16",null,1,200,100,150,true]
[null,30389,"停止排水电流比","int16",null,1,150,50,120,true]
[null,30390,"最小排水时间","int16",null,1,120,1,10,true]
[null,30391,"排水次数","int16",null,1,99,1,5,true]
[null,30392,"待机排水周期","int16",null,1,96,12,48,true]
[null,30393,"排水时间","int16",null,1,180,60,120,true]
[null,30394,"自动排水间隔","int16",null,1,999,30,150,true]
[null,30395,"高水位阈值","int16",null,1,220,30,150,true]
[null,30396,"高水位回差","int16",null,1,100,0,20,true]
[null,30397,"清洗次数","int16",null,1,10,0,1,true]
[null,30398,"制冷加湿百分比","int16",null,0.1,0,0,0,true]
[null,30399,"加湿器维护时间","int16","H",1,0,0,0,true]
[null,30400,"保留","int16",null,1,0,0,0,false]
[null,30401,"保留","int16",null,1,0,0,0,false]
[null,30402,"保留","int16",null,1,0,0,0,false]
[null,30403,"加热器数量","int16",null,1,3,0,1,true]
[null,30404,"加热进入需求","int16",null,0.1,1000,0,1000,true]
[null,30405,"保留","int16",null,1,0,0,0,false]
[null,30406,"保留","int16",null,1,0,0,0,false]
[null,30407,"保留","int16",null,1,0,0,0,false]
[null,30408,"保留","int16",null,1,0,0,0,false]
[null,30409,"保留","int16",null,1,0,0,0,false]
[null,30410,"保留","int16",null,1,0,0,0,false]
[null,30411,"保留","int16",null,1,0,0,0,false]
[null,30412,"保留","int16",null,1,0,0,0,false]
[null,30413,"单三相选择","int16",null,1,1,0,1,true,"单相：0  三相：1"]
[null,30414,"相序容错","int16",null,1,32767,-32768,0,true,"0xA1A1使能，其他值无效"]
[null,30415,"输入欠压","int16",null,1,300,80,187,true]
[null,30416,"输入过压","int16",null,1,300,80,253,true]
[null,30417,"电压回差","int16",null,1,20,0,10,true]
[null,30418,"输入频率下限","int16",null,1,65,40,48,true]
[null,30419,"输入频率上限","int16",null,1,65,40,48,true]
[null,30420,"输入电压不平衡","int16",null,0.1,1000,0,50,true]
[null,30421,"输入电压不平衡回差","int16",null,0.1,30,0,5,true]
[null,30422,"历史记录清除","int16",null,1,32767,-32768,0,true,"0xA1A1使能，其他值无效"]
[null,30423,"恢复出厂设置","int16",null,1,32767,-32768,0,true,"0xA1A1使能，其他值无效"]
[null,30424,"保留","int16",null,1,0,0,0,false]
[null,30425,"保留","int16",null,1,0,0,0,false]
[null,30426,"保留","int16",null,1,0,0,0,false]
[null,30427,"保留","int16",null,1,0,0,0,false]
[null,30428,"保留","int16",null,1,0,0,0,false]
[null,30429,"告警使能1","int16",null,1,32767,-32768,0,true,"告警使能, 位定义，RM_ALM_EN_01的Bit0对应MbIpStsEnum_t里面的第0个，bit15对应第15个，后面以此类推   \n0代表使能，1代表禁止。"]
[null,30430,"告警使能2","int16",null,1,32767,-32768,0,true," "]
[null,30431,"告警使能3","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30432,"告警使能4","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30433,"告警使能5","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30434,"告警使能6","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30435,"告警使能7","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30436,"告警使能8","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30437,"告警使能9","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30438,"告警使能10","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30439,"告警使能11","int16",null,1,32767,-32768,0,true,"//位定义，每一位对应一路AI输入，0电压信号；1电流信号\n//Bit00：AI1\n//Bit01：AI2\n//Bit02：AI3\n//Bit03：AI4\n//Bit04：AI5\n//Bit05：AI6\n//Bit06：AI7\n//Bit07：AI8\n//Bit08：保留\n//Bit09：保留\n//Bit10：保留\n//Bit11：保留\n//Bit12：保留\n//Bit13：保留\n//Bit14：保留\n//Bit15：保留"]
[null,30440,"告警使能12","int16",null,1,32767,-32768,0,true]
[null,30441,"告警使能13","int16",null,1,32767,-32768,0,true,"0xA1A1使能，其他值无效"]
[null,30442,"告警使能14","int16",null,1,32767,-32768,0,true]
[null,30443,"告警使能15","int16",null,1,32767,-32768,0,true]
[null,30444,"告警使能16","int16",null,1,32767,-32768,0,true]
[null,30445,"告警使能17","int16",null,1,32767,-32768,0,true]
[null,30446,"告警使能18","int16",null,1,32767,-32768,0,true]
[null,30447,"告警使能19","int16",null,1,32767,-32768,0,true]
[null,30448,"告警使能20","int16",null,1,32767,-32768,0,true]
[null,30449,"告警使能21","int16",null,1,32767,-32768,0,true]
[null,30450,"告警使能22","int16",null,1,32767,-32768,0,true]
[null,30451,"告警使能23","int16",null,1,32767,-32768,0,true]
[null,30452,"告警使能24","int16",null,1,32767,-32768,0,true]
[null,30453,"告警使能25","int16",null,1,32767,-32768,0,true]
[null,30454,"DO1功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30455,"DO2功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30456,"DO3功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30457,"DO4功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30458,"DO5功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30459,"DO6功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30460,"DO7功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30461,"DO8功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30462,"DO9功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30463,"DO10功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30464,"DO11功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30465,"DO12功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30466,"DO13功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30467,"DO14功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30468,"DO15功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30469,"DO16功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30470,"DO17功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30471,"DO18功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30472,"DI1功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30473,"DI2功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30474,"DI3功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30475,"DI4功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30476,"DI5功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30477,"DI6功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30478,"DI7功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30479,"DI8功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30480,"DI9功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30481,"DI10功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30482,"DI11功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30483,"DI12功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30484,"DI13功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30485,"DI14功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30486,"DI15功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30487,"DI16功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30488,"DI17功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30489,"DI18功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30490,"DI19功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30491,"DI20功能设置","int16",null,1,32767,-32768,0,true,"位定义：bit0-7：func:8;bit8-14：filter:7;bit15：inver:1;"]
[null,30492,"通用模拟输入电压电流设置","int16",null,1,0,0,0,true]
[null,30493,"保留","int16",null,1,0,0,0,false]
[null,30494,"保留","int16",null,1,0,0,0,false]
[null,30495,"保留","int16",null,1,0,0,0,false]
[null,30496,"保留","int16",null,1,0,0,0,false]
[null,30497,"保留","int16",null,1,0,0,0,false]
[null,30498,"保留","int16",null,1,0,0,0,false]
[null,30499,"保留","int16",null,1,0,0,0,false]
[null,30500,"保留","int16",null,1,0,0,0,false]
[null,30501,"保留","int16",null,1,0,0,0,false]
[null,30502,"保留","int16",null,1,0,0,0,false]
[null,30503,"保留","int16",null,1,0,0,0,false]
[null,30504,"保留","int16",null,1,0,0,0,false]
[null,30505,"保留","int16",null,1,0,0,0,false]
[null,30506,"保留","int16",null,1,0,0,0,false]

{"sheet":"设备使能","index":4,"n_rows":34,"n_cols":6,"rows_kept":34,"merged":[[1,1,1,5]]}
[]
[null,"设备使能计算表，1表示设备使能，0表示设备禁止；06功能码写"]
[null,"回风温度探头1",0,"设备使能设置寄存器","名称","值（十六进制）"]
[null,"回风温度探头2",0,30216,"设备使能1",{"$f":"DEC2HEX(C3+C4*2+C5*4+C6*8+C7*16+C8*32+C9*64+C10*128+C11*256+C12*512+C13*1024+C14*2048+C15*4096+C16*8192+C17*16384+C18*32768)","v":"0"}]
[null,"回风湿度探头1",0,30217,"设备使能2",{"$f":"DEC2HEX(C19+C20*2+C21*4+C22*8+C23*16+C24*32+C25*64+C26*128+C27*256+C28*512+C29*1024+C30*2048+C31*4096+C32*8192+C33*16384+C34*32768)","v":"0"}]
[null,"送风温度探头1",0,30218,"设备使能3",0]
[null,"送风温度探头2",0]
[null,"送风温度探头3",0]
[null,"送风湿度探头1",0]
[null,"加湿补水泵使能",0]
[null,"冷凝排水泵使能",0]
[null,"液管温度1",0]
[null,"液管温度2",0]
[null,"排气压力1探头",0]
[null,"排气压力2探头",0]
[null,"保留",0]
[null,"保留",0]
[null,"保留",0]
[null,"远程温湿度探头1",0]
[null,"远程温湿度探头2",0]
[null,"远程温湿度探头3",0]
[null,"远程温湿度探头4",0]
[null,"远程温湿度探头5",0]
[null,"远程温湿度探头6",0]
[null,"远程温湿度探头7",0]
[null,"远程温湿度探头8",0]
[null,"远程温湿度探头9",0]
[null,"远程温湿度探头10",0]
[null,"远程温湿度探头11",0]
[null,"远程温湿度探头12",0]
[null,"远程温湿度探头13",0]
[null,"远程温湿度探头14",0]
[null,"远程温湿度探头15",0]
[null,"远程温湿度探头16",0]

{"sheet":"输入端口配置","index":5,"n_rows":23,"n_cols":6,"rows_kept":23,"merged":[[1,1,1,5]]}
[null,"0:禁止;1:风机过载1;2:风机过载2;3:风机过载3;4:高压开关1;5:低压开关1;6:高压开关2;7:低压开关2;8:外风机过载1;9:外风机过载2;10:湿膜低水位;11:冷凝高水位;12:电加热过载1;13:电加热过载2;14:气流流失;15:过滤网堵塞;16:烟雾报警;17:远程开关机"]
[null,"大板输入端口配置，0表示常闭；1表示常开"]
[null,"地址","变量名称（默认功能）","枚举功能码","常开常闭","寄存器值（十六进制）"]
[null,30472,"风机过载1",1,0,{"$f":"DEC2HEX(256+D4+E4*32768)","v":"101"}]
[null,30473,"高压开关1",4,0,"104"]
[null,30474,"低压开关1",5,0,"105"]
[null,30475,"高压开关2",6,0,"106"]
[null,30476,"低压开关2",7,0,"107"]
[null,30477,"湿膜加湿低水位",10,0,{"$f":"DEC2HEX(256+D9+E9*32768)","v":"10A"}]
[null,30478,"冷凝高水位",11,1,{"$f":"DEC2HEX(256+D10+E10*32768)","v":"810B"}]
[null,30479,"电加热过载1",12,0,"10C"]
[null,30480,"电加热过载2",13,0,"10D"]
[null,30481,"气流丢失",14,0,"10E"]
[null,30482,"过滤网堵塞",15,0,{"$f":"DEC2HEX(256+D14+E14*32768)","v":"10F"}]
[null,30483,"烟火报警",16,0,"110"]
[null,30484,"室外机过载1",8,0,"108"]
[null,30485,"室外机过载2",9,0,"109"]
[null,30486,"保留",0,0,0]
[null,30487,"保留",0,0,0]
[null,30488,"保留",0,0,0]
[null,30489,"保留",0,0,0]
[null,30490,"保留",0,0,0]
[null,30491,"远程开关机",17,0,{"$f":"DEC2HEX(256+D23+E23*32768)","v":"111"}]

{"sheet":"输出端口配置","index":6,"n_rows":22,"n_cols":5,"rows_kept":22,"merged":[[2,1,2,4]]}
[]
[null,"每个DO可选的功能：0:禁止;1:内风机1;2:内风机2;3:内风机3;4:压缩机1;5:压缩机2;6:加热带1;7:加热带2;8:外风机1;9:外风机2;10:电磁阀1;11:电磁阀2;12:加湿器;13:电极进水阀;14:电极排水阀;15:湿膜进水阀;16:加热器1;17:加热器2;18:湿膜水泵;19:冷凝水泵;20:综合告警;"]
[null,"大板输出端口配置"]
[null,"地址","变量名称（默认功能）","枚举功能码","寄存器值（十六进制）"]
[null,30454,"室内风机",1,{"$f":"DEC2HEX(D5)","v":"1"}]
[null,30455,"压缩机1",4,"4"]
[null,30456,"压缩机2",5,"5"]
[null,30457,"保留",0,{"$f":"DEC2HEX(D8)","v":"0"}]
[null,30458,"加湿器",12,"C"]
[null,30459,"加湿进水阀/湿膜进水阀",13,"D"]
[null,30460,"加湿排水阀",14,"E"]
[null,30461,"加热器2",17,"11"]
[null,30462,"湿膜加湿循环水泵",18,"12"]
[null,30463,"冷凝水泵",19,"13"]
[null,30464,"保留",0,"0"]
[null,30465,"保留",0,"0"]
[null,30466,"液管电磁阀1",10,"A"]
[null,30467,"液管电磁阀2",11,"B"]
[null,30468,"加热器1",16,"10"]
[null,30469,"室外风机1",8,{"$f":"DEC2HEX(D20)","v":"8"}]
[null,30470,"室外风机2",9,"9"]
[null,30471,"报警输出",20,"14"]